## Slide 1: AIRCRAFT HANGERS

## Slide 2: Types of Hangers
Residential
Max Height - 20 ft (IBC 412.4.5)
Max Area - 2000 sq. ft ( 412.4.5)
Shall not be attached to dwelling unless separated by Not Less Than 1hr Fire Rated wall (412.4.1)
Doors – Self Closing & meet IBC 716 requirements (3/4 hr rating)(412.4.1)
Two means of egress – (412.4.2)
Smoke Alarms per IBC 907.2.2.1
Non-Residential
Over 2000 sq. ft and or Use is outside of the definition for Residential Hanger
Groups:
  Group I – Type I or Type II Const.
  Group II
  Group III – Any Type of Constructionn
  Group IV- Membrane Covered Steel Frame

## Slide 3: Types of Hangers - Continued
Residential Hanger
Plumbing , Electrical, Mechanical systems SHALL BE independent of dwelling except exterior sewer connection. (412.4.4
Storage of flammable or combustible liquid exceeding MAQ( maximum allowable quanities) – shall be in a liquid storage room ( 412.5.5)
Non-Residential
  Group I Aircraft hanger shall have at least one of the following features and operating conditions
  (1)- An Aircraft access door over 28ft
  A single fire area in excess of 40,000 sq. ft
  Provisions for housing an aircraft with tail height over 28ft
  Shall be of Type I or II construction
  At least one automatic water supply capable of supplying all required fire suppression systems, including but not limited to sprinklers syst. , foam generating systems, and hand hose lines.

## Slide 4: Types of Hangers - Continued
Residential Hanger
Exterior walls less than 30 feet to property lines or public way Shall be 2 hr rated wall- (412.3)
Fllores shall be sloped to drain-(412.3.3)
Heating Equipment shall be per (421.3.4)- Unit Heaters & Infrared Radiant heaters shall be 10ft above wing or engine
Group II Non-Residential Hanger
Group II Aircraft Hanger shall have both of the following features:
  An aircraft door height of 28 ft or less
  A single fire area for specific types of construction in accordance with Table 4.1.2
  Shall be of of any type construction
  A combination of Fire sprinkler system a, low-level low-expansion foam system or
  Closed-head foam-water sprinkler system

## Slide 5: Types of Hangers - Continued
Group I & II Hangers
Where storage and service areas are subdivided into separate fire areas they shall be separated by a wall having 2-hr fire resistive rating
Where storage and servicing is separated from office or or parts storage a 1-hr separation is required
Separation shall be provided from all sides to reduce fire exposure between buildings
Clear space of 50 ft required
Group I & II Hangers
50ft may be reduced to 25 ft when exposing wall is 2-hr min and opening protection
Where both buildings have a 3-hr fire resistive rating no separation required.
Floors shall be non-combustible and above the grade of the apron
Roof shall be class A or B
Hanger doors shall be of non-combustible material
Apron or approach shall slope away from hanger a minimum of .5 %

## Slide 6: Types of Hangers - Continued
Group I & II Hangers
Heaters shall be installed at least 10ft above the upper surface of the wings or the engine enclosure which ever is higher and not subject to damage by the aircraft
Electrical shall comply with NFPA 70 (NEC)
Group I & II Hangers
Fire Protection:
  A foam –water deluge system shall be in hangers housing single aircraft having wing area greater than 3000 sq.ft
  Combination fire sprinkler syst. And automatic low level high expansion foam syst.

## Slide 7: Types of Hangers
Residential
Fire Protection Group III Hangers NFPA 409 8.8.1.1- Fixed Fire protection shall be installed where required by and in accordance with locally adopted building codes
Portable Fire Extinguishers shall be provided in accordance with NFPA 10
Group III Non-Residential
Group III Hangers shall have both of the following:
  An aircraft access door height of 28 ft or less
  A single fire area that measures up to the maximum sq.ftg. Permitted for specific types of constrcution in accordance with Table 4.1.3
  Limited to one story
  Floor shall be non-combustible
  Hangar apron shall slope away
  Where single hangar buildings adjoin, each one has fire barrier walls with a min. rating of 2-hrs and shall not exceed the max area specified in Table 4.1.3

## Slide 8: Types of Hangers - Continued
Group III Non-Residential
Heaters shall be installed at least 10ft above the upper surface of the wings or the engine enclosure which ever is higher and not subject to damage by the aircraft
Electrical shall comply with NFPA 70 (NEC)
Fixed Fire protection shall be installed where required by and in accordance with locally adopted building codes
A minimum 6” high curbing shall be provided between each aircraft storage and service area to prevent the flow of liquid from one area to another
Egress doors for personnel not requiring the opening of doors accommodating aircraft shall be provided in each partitioned space and not exceed 150 apart.
Group III Non-Residential
Where hazardous operations including fuel transfer, welding, torch cutting, torch soldering, doping, and spray painting are performed in any Group III hangar, the hangar shall be protected with a fire protection specified in 409
Portable fire extinguishers shall be provided in accordance with NFPA 10
Roof covering shall be Class C minimum
Where single hangar buildings adjoin , each one has fire barrier walls with a minimum rating of 2 hours
Partitions separating from other spaces such as offices , shops shall have a 1-hr rating

## Slide 9: Types of Hangers - Continued
Group IV- Non- Residential
Group IV Hanger shall be any structure constructed of a membrane covered rigid frame
Membrane shall be Class A material as defined in NFPA 101
Limited to one story
Floor shall be non-combustible
Apron or approach shall slope away from hanger a minimum of .5 %
Group IV- Non- Residential
Heaters shall be installed at least 10ft above the upper surface of the wings or the engine enclosure which ever is higher and not subject to damage by the aircraft
Electrical shall comply with NFPA 70 (NEC)
Fixed Fire protection shall be installed where required by and in accordance with locally adopted building codes

## Slide 10: Types of Hangers - Continued
Fire Areas for Group II Aircraft Hangars
Const Type Single Fire Area
Type I 30,001-40,000
Type II 20,001 -40,000
Type II,III,IV 15,001- 40,000
Type II 12,001 – 40,000
Type III 12,001 – 40,000
Type V 5,000-40,000
Maximum Fire Areas for Group III Aircraft Hangars
Const Type Max Single Fire Area
Type I 30,000
Type II 20,000
Type II,III,IV 15,000
Type II 12,000
Type III 8,000
Type V 5,000

## Slide 11: Type Contruction
Type III
That type of construction in which the exterior walls are noncombustible materials and the interior building elements are of any material permitted by the code. Fire retardant treated wood framing and sheathing complying with with section 2303.2 shall be permitted within exterior wall assemblies of a 2hr rating or less
Type V
That type of construction in which the exterior walls are of any type material